## Slide 1
LAPI GANESHA UTAMA • LAB IOT & FISIKA ITB • PERTAMINA
Datasheet Sistem GLD
Spesifikasi arsitektur, interface, data flow, aplikasi, dan infrastruktur Kilang
REV 0.8 • 19 AGUSTUS 2026 • DRAFT TECHNICAL SPECIFICATION
Tangki LPG & SRU | GLD Tahap 2
Notes: [Sources]
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490
- https://github.com/fadlurrahmanf/PertaminaGLD/tree/69a493c32d2500134a21e029820cd4addea1794a
- memory/deliverables.md (audit sumber, 19 Agustus 2026)

## Slide 2
01 · SYSTEM OVERVIEW
Arsitektur operasional terdiri dari lima lapisan
Inferensi dijalankan pada GLD Node; telemetri ditransmisikan melalui LoRa dan MQTT ke aplikasi RU.
Datasheet Sistem GLD — RU IV Cilacap
2
GLD Node
8 sensor MQ + AI
→
Cluster Head
relay & cache LoRa
→
Gateway
mesh ke MQTT
→
Server RU
broker + aplikasi
→
Dashboard
monitoring operator
KILANG
Arsitektur, ATEX, cakupan gas
LAPANGAN
Perangkat, mounting, catu daya
IT PERTAMINA
Server, MQTT, keamanan jaringan
Notes: [Sources]
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §01–03
- memory/overview.md

## Slide 3
02 · IMPLEMENTATION STATUS
System status: RU NOT COMMISSIONED
ENGINEERING TEST: PASS. Hasil uji laboratorium bukan bukti operational acceptance di RU.
Datasheet Sistem GLD — RU IV Cilacap
3
Firmware integration test
PASS — 8-CH mesh dan automatic alarm push diuji di kampus
GLD power interface
BASELINE — 24 VDC ≥2 A per unit; cable dan PSU oleh RU
Mechanical mounting design
REFERENCE — L-bracket/U-clamp; no drilling; no welding
AI execution status
REPORTED ON-DEVICE — 99,20%; firmware evidence belum tersedia
RU deployment package
AVAILABLE — broker, backend, frontend, installer; not commissioned
Network integration package
AVAILABLE — MQTT contract, security baseline, go-live checklist
STATUS SISTEM
NOT COMMISSIONED — operasi RU memerlukan server, network path, site permit, dan sertifikasi hazardous-area.
Notes: [Sources]
- memory/blockers_metrics.md
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §02
- Sumber Dokumen/Summary recorder 081426 .pdf

## Slide 4
02 · INSTALLATION PREREQUISITES
Tiga prerequisite wajib ditutup sebelum instalasi
Setiap prerequisite memerlukan owner, technical approval, dan evidence of closure dari Kilang.
Datasheet Sistem GLD — RU IV Cilacap
4
1
Server & jaringan
Sediakan server/VM RU
Registrasi MAC Gateway
Satukan subnet GW + server
Tetapkan VLAN/firewall/802.1X
2
Instalasi & daya
Sediakan kabel + PSU 24VDC
Konfirmasi struktur mounting
Setujui bracket dan fastener
Verifikasi solar + baterai CH
3
Izin & sertifikasi
Sahkan TRA/JSA
Sertifikasi ATEX
Izin ketinggian permanen
Siapkan sampel gas uji
GAS-DETECTION REQUIREMENT
Tetapkan mapping Benzena, CO, dan H₂S terhadap output class model sebelum test protocol dibekukan.
Notes: [Sources]
- memory/blockers_metrics.md §Gate
- memory/decisions.md dec:30–44
- Deliverables/JSA_HSE_RU-IV_Cilacap_GLD.md (draft, belum disahkan)

## Slide 5
03 · KILANG-SUPPLIED INFRASTRUCTURE
Kilang: server, network, dan operational controls
Baseline sizing berlaku untuk pilot; final sizing mengikuti device count, data rate, retention, dan availability target.
Datasheet Sistem GLD — RU IV Cilacap
5
SERVER / VM RU
JARINGAN & OPERASI
Minimum
4 vCPU • 8 GB RAM • 100 GB SSD
Rekomendasi
8 vCPU • 16 GB RAM • 250 GB SSD
Platform
Ubuntu Server 22.04 LTS • Docker Compose
Antarmuka
1 GbE • IP stabil / reservasi DHCP • DNS/NTP
Akses
Gateway dan server dapat saling menjangkau pada VLAN yang disetujui
Keamanan
Registrasi MAC, firewall, ACL MQTT, TLS/VPN, akun servis
Operasi
PIC IT/OT, backup, retensi, monitoring, patching dan incident path
Keputusan
Host/port MQTT produksi; endpoint operator; izin koneksi VPS/HQ
PRODUCTION PARAMETERS — OPEN
Port 1884 hanya untuk bench. IT/OT Kilang wajib menetapkan port, certificate chain, DNS/IP, backup, dan retention produksi.
Notes: [Sources]
- https://github.com/fadlurrahmanf/PertaminaGLD/blob/69a493c32d2500134a21e029820cd4addea1794a/server/nodered/README.md
- https://github.com/RavellerH/gasleakdetectionV2-April/blob/660febbfceaca42ca3147fbf47ca09417bd93490/memory/PRE_INSTALLATION_HANDOFF_2026-08-05.md
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §08

## Slide 6
04 · DATA FLOW DIAGRAM
DFD-01 — akuisisi sensor hingga dashboard RU
Processing dan visualization beroperasi lokal di RU; koneksi VPS tidak menjadi dependency operasi lokal.
Datasheet Sistem GLD — RU IV Cilacap
6
01
8× MQ
sampling 1 s
→
02
ESP32-S3
AI + confidence
→
03
LoRa STAR
AES-GCM frame
→
04
CH / MESH
cache + relay
05
Gateway
LoRa → MQTT
←
06
Node-RED
decode + validate
←
07
RU Backend
GraphQL + DB
←
08
RU Frontend
operator browser
↓
NOT IMPLEMENTED
Adapter MQTT → apps/backend tidak terdapat pada repo aplikasi. Implementasi dan integration test bersifat mandatory.
Notes: [Sources]
- https://github.com/fadlurrahmanf/PertaminaGLD/tree/69a493c32d2500134a21e029820cd4addea1794a
- https://github.com/RavellerH/gasleakdetectionV2-April/blob/660febbfceaca42ca3147fbf47ca09417bd93490/memory/PRE_INSTALLATION_HANDOFF_2026-08-05.md

## Slide 7
04 · INTERFACE SPECIFICATION
Batas interface: MQTT/Node-RED → backend GraphQL
PertaminaGLD menghasilkan normalized MQTT topics; aplikasi menerima data melalui ingestion adapter.
Datasheet Sistem GLD — RU IV Cilacap
7
PertaminaGLD
gasleakdetectionV2-April
Input
gld/gateway/uplink • raw • pertamina/gld/uplink
Proses
decrypt • integrity • replay • topology
Output
decoded • alarm • status • events • integrity
Input wajib
adapter mengubah MQTT normalized → addReading/device
Layanan
NestJS GraphQL • Prisma • database RU
Konsumen
Next.js dashboard • map • alerts • analytics
MQTT NORMALIZED →
MANDATORY DATA CONTRACT
deviceId • timestamp • gasClass/aiClass • confidence • battery • network/health • messageId untuk deduplication.
Notes: [Sources]
- https://github.com/fadlurrahmanf/PertaminaGLD/blob/69a493c32d2500134a21e029820cd4addea1794a/server/nodered/README.md
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps/backend

## Slide 8
05 · APPLICATION SPECIFICATION
Frontend — RU operator UI dan HQ read-only UI
IMPLEMENTED: Next.js client dengan GraphQL polling. GraphQL subscription tidak diimplementasikan.
Datasheet Sistem GLD — RU IV Cilacap
8
FRAMEWORK
Next.js 15 • React 18 • TypeScript
VISUALISASI
Mapbox GL • Recharts • Tailwind CSS
DATA ACCESS
GraphQL Request → endpoint RU :4000/graphql
REFRESH
Polling berkala; default setting 10 detik
MODUL
Overview • Devices • Map • Alerts • Events
ANALITIK
Timeline sensor • confidence • status perangkat
MODE RU
Operasional lokal termasuk menu admin/settings
MODE HQ
Read-only; mutation dan settings disembunyikan
KILANG-SUPPLIED ACCESS
Kilang menetapkan internal URL, DNS/IP, TLS certificate, identity/access policy, operator workstation, dan availability target.
Notes: [Sources]
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps/frontend
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps/ru-frontend

## Slide 9
05 · APPLICATION SPECIFICATION
Backend: ingestion, storage, dan API GraphQL
IMPLEMENTED RU: SQLite. PostgreSQL/TimescaleDB belum menjadi production baseline yang disetujui.
Datasheet Sistem GLD — RU IV Cilacap
9
RUNTIME/API
Node.js • NestJS • Apollo GraphQL • port 4000
DATA LAYER
Prisma ORM • current RU schema: SQLite file-based
CORE ENTITIES
Device • GasReading • SystemSettings • EventLog • User
INGESTION
addReading validates confidence 0–1 and derives LOW/MIDDLE/HIGH
ALERT LOGIC
Threshold default warning 0.70 • critical 0.80 • dedup 15 menit
API
dashboard • devices • timeline • events • analytics • gatewayPull
SECURITY STATE
Production hides playground/introspection; CORS still broad
OPEN ITEM
MQTT adapter, backup/retention RU, auth/TLS and hardening
DATABASE BASELINE — OPEN
Tetapkan SQLite untuk pilot atau migrasi PostgreSQL. Keputusan wajib mencakup sizing, backup, retention, HA, dan recovery objective.
Notes: [Sources]
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps/backend
- https://github.com/RavellerH/gasleakdetectionV2-April/blob/660febbfceaca42ca3147fbf47ca09417bd93490/apps/backend/prisma/schema.prisma

## Slide 10
06 · INTER-SITE INTEGRATION
DFD-02: RU → VPS/HQ (NOT COMMISSIONED)
RU beroperasi mandiri; VPS menarik data read-only melalui VPN. Remote actuation tidak termasuk scope fase ini.
Datasheet Sistem GLD — RU IV Cilacap
10
RU Backend
SQLite lokal
→
gatewayPull
GraphQL + auth
→
VPN
private route
→
Gateway VPS
pull tiap 30 s
→
PostgreSQL
7 / 90 hari
→
HQ Frontend
read-only
VPS RETENTION TARGET
Reading dan non-critical event: 7 hari. Critical event: 90 hari. Final retention policy memerlukan approval Kilang.
NOT COMMISSIONED
Gateway service tersedia di repo. Production deployment, VPN, credential, DNS, backup, dan monitoring belum diverifikasi.
Notes: [Sources]
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps/gateway
- https://github.com/RavellerH/gasleakdetectionV2-April/blob/660febbfceaca42ca3147fbf47ca09417bd93490/memory/PRE_INSTALLATION_HANDOFF_2026-08-05.md

## Slide 11
07 · FIELD DEVICE SPECIFICATION
GLD Node: hardware, firmware, dan telemetri
Firmware v0.8.14 • 8-channel MQ acquisition • on-device inference • 24 VDC ≥2 A.
Datasheet Sistem GLD — RU IV Cilacap
11
MCU
ESP32-S3-WROOM-1U-N16R8
ADC
ADS1256, 24-bit
SENSOR
8 × MQ
TELEMETRI
LoRa tiap 10 detik
ALARM
gasClass ≠ 0; confidence ≥30%
KEAMANAN FRAME
AES-128-GCM, 39 byte
AI
CNN Dual-Branch, int8
CATU DAYA
24VDC ≥2A per unit
MOUNTING
L-bracket referensi Emerson
* 99,20% berasal dari laporan model int8. On-device execution memerlukan traceability ke firmware commit dan binary release.
Notes: [Sources]
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §04
- memory/entities.md §Model AI
- memory/decisions.md dec:39–43

## Slide 12
07 · FIELD DEVICE SPECIFICATION
Cluster Head dan Gateway — functional specification
Cluster Head menyediakan cache/relay LoRa; Gateway menyediakan LoRa-to-MQTT bridge. Seluruh buffer bersifat volatile.
Datasheet Sistem GLD — RU IV Cilacap
12
CLUSTER HEAD
GATEWAY
Dual SX1262
STAR ke GLD + MESH ke CH/Gateway
Cache 32 node
Failover parent otomatis berbasis RSSI
2 panel solar + 18650
Surplus daya 1,5–4,4 Wh/hari
16 unit tersedia
9 CH besar + 7 CH kecil
Radio mesh 921,0 MHz
SF9 • 17 dBm
Bridge Wi-Fi/LAN ke MQTT
MAC didaftarkan; satu subnet dengan server
Buffer 8 item RAM
Volatil, bukan penyimpanan permanen
Unit indoor
Antena ditempatkan outdoor/rooftop
CAPACITY LIMIT — OPEN
Maximum supported GLD Node per Cluster Head dan per Gateway belum ditetapkan melalui load test.
Notes: [Sources]
- memory/blockers_metrics.md §Status produksi unit
- memory/blockers_metrics.md §Gate capacity
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §04

## Slide 13
08 · RF SPECIFICATION
STAR dan MESH menggunakan domain radio terpisah
Frekuensi, spreading factor, dan sync word dikonfigurasi berbeda untuk mengisolasi kedua link.
Datasheet Sistem GLD — RU IV Cilacap
13
PARAMETER
STAR — GLD ↔ CH
MESH — CH ↔ GW
Frekuensi
920,0 MHz
921,0 MHz
Spreading Factor
SF7
SF9
TX power
17 dBm
17 dBm
Sync word
0x12
0x34
100 m terbuka
PDR 100%
242 m Gerbang Utara
PDR 100%
200 m terhalang gedung
PDR 87%
Notes: [Sources]
- memory/blockers_metrics.md §Metrik RF LoRa
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §05

## Slide 14
09 · HAZARDOUS-AREA COMPLIANCE
Instalasi permanen dilarang sebelum sertifikasi
Enclosure menggunakan dua kompartemen dengan seal/cable gland; compliance ATEX belum diverifikasi.
Datasheet Sistem GLD — RU IV Cilacap
14
INSTALLATION HOLD
ATEX certificate dan elevated-mounting approval belum tersedia. Permanent installation tidak diizinkan.
MODUL ELEKTRONIK
PCB + power di enclosure Ex-Proof
SEAL / CABLE GLAND →
SENSOR CARTRIDGE
Elektronik sensor di kompartemen terpisah
Non-intrusive mounting
L/U-bracket pada existing structure; drilling dan welding dilarang
Hazardous-area power protection
24 VDC protection wajib sesuai zone; Gateway ditempatkan di safe area
Notes: [Sources]
- Sumber Dokumen/Summary recorder 081426 .pdf
- Sumber Dokumen/Notulensi_Rapat_5Agustus2026_GLD.pdf
- memory/deliverables.md (koreksi audit: 2 kompartemen + seal/gland)

## Slide 15
10 · GAS DETECTION AND AI
Model AI tidak mencakup tiga gas requirement RU
Current model classes: LPG, CO₂, H₂, dan clean air. Benzena, CO, dan H₂S tidak tercakup.
Datasheet Sistem GLD — RU IV Cilacap
15
AKURASI MODEL INT8
99,20%
UJI REAL-TIME
97,65%
UKURAN MODEL
9,14 KB
KELAS MODEL SAAT INI
LPG
CO₂
H₂
Udara Bersih
REQUIREMENT BELUM DICAKUP
Benzena
CO
H₂S
Metana belum tervalidasi
Notes: [Sources]
- Sumber Dokumen/06 Aguatus Deteksi_Kebocoran_Gas_CNN_DualBranch (2) - Repaired.pptx
- Sumber Dokumen/Notulensi_Rapat_5Agustus2026_GLD.pdf
- memory/entities.md §Model AI

## Slide 16
11 · RU DEPLOYMENT SPECIFICATION
RU services pada server/VM internal Kilang
Port yang ditampilkan adalah current repo/bench defaults. Production firewall rules ditetapkan IT/OT Kilang.
Datasheet Sistem GLD — RU IV Cilacap
16
INGRESS
MQTT 1884* • Node-RED 1880
→
BACKEND
GraphQL 4000 • database lokal
→
FRONTEND
RU web 3002 • browser operator
RUNTIME
Docker Compose
RU DATABASE SAAT INI
SQLite
HQ GATEWAY
4100 + PostgreSQL
MINIMUM FIREWALL POLICY
Allow: Gateway→MQTT, operator→frontend, frontend→backend, dan RU→VPS via VPN jika disetujui. Deny public access ke Node-RED admin.
Notes: [Sources]
- https://github.com/RavellerH/gasleakdetectionV2-April/tree/660febbfceaca42ca3147fbf47ca09417bd93490/apps
- https://github.com/fadlurrahmanf/PertaminaGLD/blob/69a493c32d2500134a21e029820cd4addea1794a/server/nodered/README.md

## Slide 17
12 · POWER SPECIFICATION
Baseline 24 VDC; portable battery tidak digunakan
Cluster Head menggunakan dual solar panel dan 18650 battery; hazardous-area certification belum tersedia.
Datasheet Sistem GLD — RU IV Cilacap
17
GLD NODE
CLUSTER HEAD
Input 24 VDC ≥2 A per unit
Production power baseline
Cable dan PSU disediakan RU
Satu protected circuit per installation point
Portable battery excluded
Measured endurance 1,76 hari; requirement 30 hari
Dual-panel energy surplus
Calculated surplus 1,5–4,4 Wh/hari
Panel → BQ25185 → 18650
TPS63020 3,3V menuju beban
Solar/battery certification unavailable
Hazardous-area verification mandatory
Baterai GLD: 1,76 / 30 hari
Notes: [Sources]
- memory/blockers_metrics.md §Metrik daya
- memory/decisions.md dec:39–41
- Sumber Dokumen/Timeline_Kerjaan_Mingguan_GLD_updated_Juli_2026.pdf

## Slide 18
13 · COMMISSIONING PREREQUISITES
Delapan open item memblokir commissioning
Tidak ada open item pada slide ini yang dapat ditutup hanya dengan hasil uji laboratorium.
Datasheet Sistem GLD — RU IV Cilacap
18
TRA/JSA approval
OPEN — internal draft only
ATEX certification
OPEN — permanent installation prohibited
MQTT ingestion adapter
NOT IMPLEMENTED
Gateway/server network approval
OPEN — VLAN, ACL, identity, firewall
Elevated-mounting approval
OPEN — test limited to human height
Gateway/CH capacity limit
OPEN — load test not available
RU production database
OPEN — SQLite pilot vs PostgreSQL
RU server/VM allocation
OPEN — resource confirmation required
PROGRESS BOUNDARY
≈39% merepresentasikan engineering laboratory progress; tidak merepresentasikan certification, commissioning, atau operational acceptance.
Notes: [Sources]
- memory/blockers_metrics.md §Gate
- memory/overview.md (baseline progres)
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §10

## Slide 19
14 · ACCEPTANCE CRITERIA
Minimum commissioning acceptance criteria
Sistem hanya dapat dinyatakan operational setelah seluruh evidence diverifikasi di RU.
Datasheet Sistem GLD — RU IV Cilacap
19
1
SITE READINESS
TRA/JSA approved; mounting structure released; protected 24 VDC circuit available.
2
SYSTEM INTEGRATION
Server/VM allocated; network path approved; MQTT adapter and RU database operational.
3
SAFETY COMPLIANCE
ATEX approval issued; required gas classes validated; permanent installation authorized.
MANDATORY EVIDENCE
MQTT broker online; ingestion tervalidasi; alarm tampil di dashboard; restore test lulus; hazardous-area approval diterbitkan.
Notes: [Sources]
- Deliverables/Datasheet_Sistem_GLD_Arsitektur_ServerJaringan.html §08–11
- memory/blockers_metrics.md
- memory/deliverables.md